[image: image1.emf]







[image: image2.emf][image: image3.jpg]




Approval Drawings

​Series

OHV
Commercial Unit Heater
[image: image4.jpg]ah-

us
VERSION OFFERTE







Features

Color
-
Standard: almond.
Finish
-
Standard: epoxy/polyester powder paint.
Voltage
-
208V, 240V, 277V, 347V, 480V, 600V, 1 or 3-phase.

Construction
-
Draw-through design for more evenly heated air.


-
Specially designed outlet diffuser provides maximum 



air velocity.


-
Individually adjustable louvers to direct discharge air flow.


-
High-limit temperature control with automatic reset.

-
18 and 20 gauge steel.
Fan
-
Motor - totally enclosed - thermally protected.


-
Motor mounted in ambient air stream, 



shielded from heating elements.

-
Fan delay purges heater of residual heat for longer life.
Heating element
-
Stainless steel sheath with aluminum fins.

· Draw-through design permits greater heat transfer.
Control
-
All models have factory installed contactor.

· 24V control circuit standard on all models (except 2, 3 & 5kW, 208/240V heaters).

· 2, 3 & 5kW, 208/240V heaters have 208/240V control (24V control available).
· Full line of unit mounted control accessories available (factory or field installed).

Installation
-
Minimum mounting height of 6 ft. (1.8 m.)

· Horizontal or vertical discharge air flow.

· Includes wall and ceiling mounting brackets (for horizontal discharge air flow).

· For vertical air flow 4 welded nuts (for threaded rod 3/8 in. X 16 UNC) 
provided in heater back.

· Large and easily accessible control compartment.
Note: We recommend installing this product on an outside ceiling or wall to avoid vibrations spreading to an adjacent room.
Warranty
-
5-year warranty against defects.

Application 
-
Factory, warehouse, garage, store, shipping room.
[image: image5.jpg]@DUELLET




Models

	Product #
	Qty
	Volts (ph)
	kW
	Control

Voltage
	BTU/hr
	cfm
	Temperature Rise
	Motor

	
	
	
	
	
	
	
	°C
	°F
	HP
	rpm

	OHVU02008AM
	
	208 (1/31)
	2.0 
	240/208
	6824
	310
	11
	20
	1/50
	1490

	OHVU03008AM
	
	208 (1/31)
	3.0 
	240/208
	10236
	310
	17
	31
	1/50
	1490

	OHVU05008AM
	
	208 (1/31)
	5.0 
	240/208
	17060
	310
	28
	50
	1/50
	1490

	OHVU07508AM-24
	
	208 (1/31)
	7.5 
	24
	25590
	600
	22
	40
	1/33
	1490

	OHVU09908AM-24
	
	208 (1/31)
	9.9 
	24
	33780
	600
	29
	52
	1/33
	1490

	OHVU15038AM-24
	
	208 (3)
	15 
	24
	51180
	915
	29
	52
	1/8
	1490

	OHVU02000AM
	
	240/208 (1/31)
	2.0/1.5
	240/208
	6824/5118
	310
	11
	20
	1/50
	1550

	OHVU03000AM
	
	240/208 (1/31)
	3.0/2.3
	240/208
	10236/7848
	310
	17
	31
	1/50
	1550

	OHVU05000AM
	
	240/208 (1/31)
	5.0/3.75
	240/208
	17060/12966
	310
	28
	50
	1/50
	1550

	OHVU07500AM-24
	
	240/208 (1/31)
	7.5/5.6
	24
	25590/19200
	625
	21
	38
	1/33
	1550

	OHVU10000AM-24
	
	240/208 (1/31)
	10.0/7.5
	24
	34120/25590
	625
	28
	50
	1/33
	1550

	OHVU15000AM-24
	
	240/208 (1/31)
	15.0/11.3
	24
	51180/38387
	950
	28
	50
	1/8
	1550

	OHVU15030AM-24
	
	240/208 (3)
	15.0/11.3
	24
	51180/38387
	950
	28
	50
	1/8
	1550

	OHVU19830AM-24
	
	240/208 (3)
	19.8/14.9
	24
	67560/50840
	1300
	27
	49
	1/8
	1550

	OHVU20000AM-24
	
	240/208 (1/31)
	20.0/15.0
	24
	68240/51180
	1300
	27
	49
	1/8
	1550

	OHVU20038AM-24 
	
	208 (3)
	20.0
	24
	68240
	1250
	28
	50
	1/8
	1490

	OHVU02077AM-24
	
	277 (1)
	2.0
	24
	6824
	310
	11
	20
	1/50
	1550

	OHVU03077AM-24
	
	277 (1)
	3.0
	24
	10236
	310
	17
	31
	1/50
	1550

	OHVU05077AM-24
	
	277 (1)
	5.0
	24
	17060
	310
	28
	50
	1/50
	1550

	OHVU07577AM-24
	
	277 (1)
	7.5
	24
	25590
	625
	21
	38
	1/33
	1550

	OHVU10077AM-24
	
	277 (1)
	10.0
	24
	34120
	625
	28
	50
	1/33
	1550

	OHVU02034AM-242
	
	480 (3)
	2.0
	24
	6824
	310
	11
	20
	1/50
	1550

	OHVU03034AM-242
	
	480 (3)
	3.0
	24
	10236
	310
	17
	31
	1/50
	1550

	OHVU05034AM-242
	
	480 (3)
	5.0
	24
	17060
	310
	28
	50
	1/50
	1550

	OHVU07534AM-242
	
	480 (3)
	7.5
	24
	25590
	625
	21
	38
	1/33
	1550

	OHVU10034AM-24
	
	480 (3)
	10.0
	24
	34120
	625
	28
	50
	1/33
	1550

	OHVU15034AM-24
	
	480 (3)
	15.0
	24
	51180
	950
	28
	50
	1/8
	1550

	OHVU20034AM-24
	
	480 (3)
	20.0
	24
	68240
	1300
	27
	49
	1/8
	1550

	
	
	
	
	
	
	
	
	
	
	


1 Models with the indication "1/3" can be field converted from 1 to 3-phase.
2 480V, 1-phase available upon request. 

Remember to change the 3 for 0 when ordering. E.g.: OHVU05034AM-24 becomes OHVU05004AM-24.

600V available upon request. 

Mounting hardware included.

Standard color is almond.
Options
	Product #

Kit
	Product # 

Factory installed*
	Description
	Qty

	-
	120
	120V control circuit
	

	-
	24
	24V control circuit
	

	-
	3P
	Triple-pole contactor
	

	KIT-OHV-D41
	D41
	Disconnect switch, triple-pole, 40A
	

	KIT-OHV-D81
	D81
	Disconnect switch, triple-pole, 80A
	

	KIT-OHV-F1
	F1
	Continuous fan switch, for 2 to 5kW units
	

	KIT-OHV-F2
	F2
	Continuous fan switch with 24V relay, for units with 24V control circuit
	

	KIT-OHV-F3
	F3
	Continuous fan switch, for less than 480V units (7.5 to 20kW)
	

	KIT-OHV-F4
	F4
	Continuous fan switch, for 480V units and over (7.5 to 20kW)
	

	KIT-OHV-FR
	FR
	Unit mounted fan relay for remote fan control of heaters with 24V control circuit
(remote fan switch not included)
	

	-
	FUS
	Branch circuit fusing
	

	-
	HL
	Hi/Lo switch (15 to 20kW)
	

	KIT-OHV-R
	R
	24V relay, without transformer
	

	KIT-OHV-RT
	RT
	24V relay, with transformer
	

	KIT-OHV-T2S
	T2S
	2-stage thermostat (15 to 20kW)
	

	KIT-OHV-T5
	T5
	Single-stage thermostat, for 10kW units and less
	

	KIT-OHV-T6
	T6
	Single-stage thermostat, for units over 10kW
	


* For factory installed options, add the option number to the product number. See the Product Code section inside the front cover. 

1 For the U.S. only: The nominal current of the unit must not exceed 80% of the capacity of the disconnect. 

Others
	Type
	Quantity
	Model and description

Complementary information
	Volts
	Phase
	Watts
	Length

mm/in.
	Information
Color/installation

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


Specifications may change without prior notice

	Project:
	Approval

Information

	Consultant Engineer:
	

	Electrician Contractor:
	

	Distributor:
	

	Date :
	

	Contact in Ouellet:
	

	Comments:


180, 3e Avenue, L’Islet (Québec) G0R 2C0 CANADA • Phone: 1 800 463-7043 • Fax: 1 800 662-7801 • info@ouellet.com • www.ouellet.com

