[image: image1.png]uonedyIds spdureg
SI[I0g AN -I[qIXd] ueArg




CLM, HECLM, K & RV Series 

Water & Steam Boilers – Configuration Packages

“Knockdown” Type

CLM, HECLM, K & RV Series 

Water & Steam Boilers – Configuration Packages

“Knockdown” Type


ATMOSPHERIC:
CLM & K SERIES:

KD-1

The boiler is shipped as an assembled unit, with the ability to be disassembled and reassembled at the job site.  The boiler vessel, with tubes installed, is bolted (not welded) to the base.  The burner tray assembly and controls are mounted and wired.  However, the boiler does not need to be disassembled before it can be started-up and operated.

KD-2

The boiler is shipped partially disassembled in two crates.  The boiler vessel, with tubes installed, is bolted (not welded) to the boiler base with the burner tray assembly installed is shipped as one piece.  The boiler flue collector, jacket, and controls are all removed and shipped as the second piece.  Both pieces are crated separately and shipped for job site assembly.

KD-3

The boiler is shipped the same as the KD-2, except that the tubes are shipped loose as the third piece, which will be separately crated and shipped for job site assembly.  Comes with a tube driver and puller.

KD-6

This configuration would indicate a special knockdown design other than those listed above.  Please specify your exact requirements and consult the factory for pricing and availability.
FORCED DRAFT:
CLM & HECLM SERIES:

KD-1

The boiler is shipped as a completely assembled unit, but constructed to be knocked-down at the job site.  The boiler vessel, with tubes installed, is bolted (not welded) to the base.  The boiler requires some finishing brickwork to be completed, therefore, partial disassembly and reassembly at the job site is required prior to starting and operating the boiler.

KD-2


The boiler will be shipped as a partially disassembled unit.  The boiler vessel, with tubes installed, is one piece.  The boiler base with 

refractory and burner mounted is the second piece.  The boiler flue collector, jacket and controls are the third portions.  All three pieces are crated separately for job site assembly.

KD-3


The boiler will be shipped the same as the KD-2 unit, except that the tubes are shipped loose as a fourth portion, which is separately crated and shipped for job site assembly.  Comes with a tube puller and driver.

KD-6

This configuration would indicate a special knockdown design other than those listed above.  Please specify your exact requirements and consult the factory for pricing and availability.

NOTE:
1. Complete written instructions are provided for reassembling with each of the “KD” boilers.

2. In cases where it is known that the boiler components may be lowered through a shaft or small opening by a crane, special bracing or lifting lugs may be required in a position other than standard.  Please contact the factory for additional pricing.

3. It is strongly recommended that the installing contractor review our “KD” written instructions prior to disassembly and/or reassembly of any of our “KD” boilers.  For RV boiler, also review the RV “KD” video.

4. No UL boiler package label is available with knockdown boilers.


FORCED DRAFT:
RV Series:

KD-4

The boiler is shipped as a completely assembled unit, but constructed to be knocked-down at the job site.  The boiler vessel, with flanged downcomers and tubes installed, is mounted to its base.  The boiler must be disassembled and then reassembled at the job site before it can be started up and operated.  During reassembly construction, the contractor will be required to pour the refractory floor and reinstall all the components.  A welder is required, but no ASME code welding is needed.  Care should be taken to observe disassembly procedure, since reassembly is exactly the reverse procedure.  Comes with a tube puller and driver.

KD-5

The boiler is shipped as a completely disassembled unit for job site assembly.  The boiler vessel is shipped with the tubes and the flanged middle downcomers shipped loose.  The upper header is bolted to the lower header and shipped as one piece, mounted to the base.  The burner and controls are shipped separately as a second piece.  The boiler flue collector and jacket are shipped as the third piece, and the tubes are shipped as the fourth.  The pieces are crated separately and shipped to the job site for assembly.  During assembly construction, the contractor will be required to pour the refractory floor, assemble the boiler vessel, install the tubes, and all other components.   A welder is required, but no ASME code welding is needed.  Comes with a tube puller and driver.

KD-6

This configuration would indicate a special knockdown design other than those listed above.  Please specify your exact requirements and consult the factory for pricing and availability.

NOTE:
1. Complete written instructions are provided for reassembling with each of the “KD” boilers.

2. In cases where it is known that the boiler components may be lowered through a shaft or small opening by a crane, special bracing or lifting lugs may be required in a position other than standard.  Please contact the factory for additional pricing.

3. It is strongly recommended that the installing contractor review our “KD” written instructions prior to disassembly and/or reassembly of any of our “KD” boilers.  For RV boiler, also review the RV “KD” video.

4. No UL boiler package label is available with knockdown boilers.

Form 2218

    ( Rev 11/10/04  (  Repl 03/01/04 (
    Page 1 of 2
Form 2218                                                     ( Rev 11/10/04  (  Repl 03/01/04 (
    Page 2 of 2

