[image: image1.wmf]UW Series 

U-Tube Heat Exchangers

Water to Water Type

[image: image2.png]uonedyIds spdureg
SI[I0g AN -I[qIXd] ueArg







The hot water heater shall be a Bryan Model UW _______________ shell and tube heat exchanger, with a capacity to ________ heat _____ GPM of water from _____oF to _____oF with _____ GPM of water at _____ oF and  with a fouling factor of 0.0005.  The velocity should be no more than 7 feet/second to avoid premature failure and proper operation.  The heat exchanger shall have less than 10 PSIG pressure drop.  The U-tube heat exchanger shall be either a 2-pass or 4-pass design for maximum efficiency and minimal length.

VESSEL CONSTRUCTION

The heat exchanger shell shall be constructed of steel and be a minimum of 4” in diameter to maximum of 12” in diameter.  The shell shall be designed and constructed in strict accordance with ASME Heating Code, Section VIII, and shall bear the ASME stamp for a maximum working pressure of 150 PSIG and a maximum operating temperature of 375oF.

HEAT EXCHANGER CONSTRUCTION

The U-tube heat exchanger heating element shall be constructed of heavy indirect copper coil manufactured of seamless ¾” O.D. tubing and shall have a maximum design pressure of (125 or 150) PSIG.  The heat exchanger shall be attached to the shell by means of a cast iron head minimum pressure rating of 125 PSIG with a gasket and stud type connection and shall be easily removable and replaceable.

The complete unit shall be tested at the factory before shipment to ensure a proper fitting with no leaks.

The inlet and outlet of the shell shall be sized for minimal pressure drop and be threaded for connections less than 4” and be flanged for sizes greater than 3”.

OPTIONAL EQUIPMENT

1. Heat exchanger saddle base

2. Bronze or stainless tube sheets

3. Oversize collars

Form 2229

( Rev 02/01/04  (  Repl New (
    Page 1 of 1

